Dukovany Load Follow Benchmark

Daneš Burket, NPP Dukovany

burked1.edu@mail.cez.cz

( +420 618 814 665

General description of the tests

The test were performed during cycle 11 of Unit 2 of Dukovany NPP, which unit is a VVER-440 type V-213. The test starts at 125 FPD. During the tests the plat was maneuvring in secondary and tertiary control modes, the goal was to collect data to test transient calculations. There were six tests comprising various power changes, see Fig. 1. All relevant parameters (power, temperature rise, control rod position, inlet temperature, boron acid concentration) were put down by step by step after every change of these parameters, see Tab. 3. A large data set was obtained for load follow analyses which can be used for testing of neutronic codes. The detailed description of these tests is given below.

The tests start: Unit 2, Cycle 11, 125 FPD. The core map is given in Fig. 2, the assembly types in Fig. 3, the assembly-wise burnup and power distribution at the start of the experiment are given in Fig. 4.

Test No. 1: Test of secondary control mode (SCM) with interval of power change 20 %

The test consists of four phases.

1.	Powers of both turbo-generators (TG) decrease with trend 1 %/min. to level corresponding to 80 % reactor power,

2.	Stabilization,

3.	Powers of both TGs increase with trend 1 %/min. to level corresponding to 100 % reactor power,

4.	Stabilization.

Test No. 2: Test of SCM with cyclic power changes 10 % (constant main steam collector pressure)

1.	Powers of both TGs decrease with trend 1 %/min. to level corresponding to 90 % reactor power,

2.	Stabilization,

3.	Powers of both TGs increase with trend 1 %/min. to level corresponding to 100 % reactor power,

4.	Stabilization,

5.	Powers of both TGs decrease with trend 1 %/min. to level corresponding to 90 % reactor power,

6.	Powers of both TGs increase with trend 1 %/min. to level corresponding to 100 % reactor power,

7.	Stabilization.

Test No. 3: Test of SCM with cyclic power changes 10 % (constant mean temperature)

1.	Powers of both TGs decrease with trend 1 %/min. to level corresponding to 90 % reactor power,

2.	Powers of both TGs increase with trend 1 %/min. to level corresponding to 100 % reactor power,

3.	Powers of both TGs decrease with trend 1 %/min. to level corresponding to 90 % reactor power,

4.	Powers of both TGs increase with trend 1 %/min. to level corresponding to 100 % reactor power,

5.	Stabilization.

Test No. 4: Test of tertiary control mode (TCM) with reactor power decrease to level 55 %

1.	7.5 % power decrease with 0.5%/min. trend, followed by 10 min. stabilization pauses step by step to reactor power level 55 %,

2.	Stabilization,

3.	7.5 % power increase with 0.5%/min. trend, followed by 10 min. stabilization pauses step by step to reactor power level 100 %,

4.	Stabilization.

Test No. 5: Test of TCM with reactor power decreasing to level 55 % (constant main steam collector pressure)

1.	7.5 % power decreasing with 0.5%/min. trend, followed by 10 min. stabilization pauses step by step to reactor power level 55 %,

2.	Stabilization,

3.	7.5 % power increasing with 0.5%/min. trend, followed by 10 min. stabilization pauses step by step to reactor power level 88 %,

4.	Stabilization.

Test No. 6: Test of primary circuit thermohydraulics charakteristics

1.	Stabilization on reactor power level 88 %,

2.	Reactor power decreasing to level 83 % (power jump),

3.	Primary circuit pump (PCP) No. 6 switching off with reactor power decrease to level 75 %,

4.	Reactor power increasing to level 78 %,

5.	Stabilization,

6.	PCP No. 6 switching on,

7.	7.5 % power increasing of both TG with trend 0.5 %/min. step by step with 10 min. pauses after every step to reactor power level 88 %.

Stabilization

A course of the following xenon transient process (( 12 hours) was put down for needs of xenon processes analyses. The stabilization is in this meaning course with „constant“ power (within a ( 1 % wide range).

Power levels in general description above are only for orientation - it is only general preview of the tests. The exact values see in Tab. 3.

Measurement description

Relevant measured values were obtained by standard methods used on VVER 440 plants. Boron concentration was assigned by a titration method with error ± 0.05 g/kg (on line boron measurement was not in operation). Bank 6 position was measured by a position indicator with error ± 1 cm. Reactor power was calculated from loop DT and flow rate values, calculations were performed on a VK3 computer. Tin is average from 6 measurements (thermocouples) in cold loops.

Initial burnup and power distributions were calculated by the MOBY-DICK code (See Fig. 4, Tab. 1 and 2). The MOBY-DICK geometrical representation of the core contains 20 axial and 24 radial segments for each assembly. In Table 2, the first layer contains structural material in a control assembly. Two-group WIE62GQ5 library was used. The reload schemes and other input data for MOBY-DICK are not given here since burnup distribution error must have a minor effect on the control group position H6 as the latter is a global characteristics of the core.

How to use the test

Use data in Tab. 3 as input to your transient model and determine either keff or H6. If |keff-1| < 0.1 then your code is acceptable if your H6 differs from column Bank6 by at most 10 cm, your code is acceptable.

Fig. 1: Power Changes During the Tests (from (T)

Fig. 2: Core map (60( symetry)

Fig. 3: Material Description (for detailed description see [3])

Assembly No.  59 3( 4(  ((-enrichment 3-3.6%, 2-2.4%)

kq  .349    ((- year of assembly operation)

Burn-up [MWd/t]  34044     (*- assembly which was 1 year in pool)

57 3 1 58 3 1

.994   .717

EFFECTIME TIME = 125 DAYS         4068   2905

BAC = 3.169 g/kg             53 3 1 54 3 1 55 3 3 56 3 4

TOTAL POWER = 1375 MW         1.253  1.166   .692   .367

5177   4836  26199  32748

48 3 1 49 3 4 50 3 1 51 3 1 52 3 3

1.260   .996  1.207  1.034   .495

5159  33490   5336   4304  25800

42 3 3 43 3 4 44 3 2 45 3 2 46 3 1 47 3 3

1.012   .960  1.198  1.231  1.101   .499

27139  34598  14992  12697   4600  25149

35 3 2 36 3 3 37 3 3 38 3 2 39 3 2 40 3 1 41 3 4

1.211  1.060  1.053  1.224  1.230  1.034   .368

14151  24296  26196  15075  12703   4305  32715

28 3 2 29 3 3 30 3 2 31 3 3 32 3 2 33 3 1 34 3 3

1.223  1.090  1.099  1.052  1.196  1.206   .692

16884  26318  17257  26192  15002   5332  26204

20 3 5 21 3 2 22 3 3 23 3 3 24 3 4 25 3 4 26 3 1 27 3 1

1.115  1.236  1.090  1.059   .957   .995  1.166   .716

27088  15226  26321  24299  34848  33492   4834   2903

11 3 3 12 3 5*13 3 2 14 3 2 15 3 3 16 3 1 17 3 1 18 3 1 19 3 4

1.139  1.115  1.224  1.212  1.011  1.259  1.253   .994   .347

24505  27091  16900  14175  27197   5157   5178   4067  34544

1 2 4  2 3 2  3 3 2  4 3 2  5 3 3  6 3 2  7 2 3  8 3 4  9 3 3 10 2 3

.700  1.226  1.219  1.178  1.140  1.141   .671   .934   .901   .479

28973  15002  17264  17648  24305  16863  24374  35826  27305  23753

Fig. 4: Power and Burn-up Distribution (Calculated by MOBY-DICK)

Tab. 1: Axial Relative Power Distribution

(Calculated by MOBY-DICK, accuracy 7 %)

20 - top of core

1 - bottom core

1    2    3    4    5    6    7    8    9   10   11   12   13   14   15   16   17   18   19   20

20       0  550  627    0  601  521    0  421  463    0  603  612  644  617  478  506  548  449  170  612

19       0  781  901  932  853  737    0  586  636  356  841  863  922  874  669  741  807  657  257  863

18       0  995 1091 1097 1025  934    0  741  776  429 1011 1029 1111 1060  841  971 1018  829  313 1029

17       0 1116 1204 1206 1126 1045    0  832  865  481 1113 1122 1221 1174  933 1112 1162  945  347 1123

16       0 1265 1273 1271 1187 1180    0  946  927  515 1179 1177 1286 1248 1051 1281 1263 1023  369 1177

15       0 1296 1315 1309 1225 1208    0  976  964  537 1218 1208 1325 1294 1070 1327 1330 1075  383 1209

14    1065 1351 1347 1334 1255 1261 1014 1033 1000  552 1254 1228 1350 1335 1121 1396 1391 1113  392 1228

13    1093 1398 1364 1347 1272 1303 1048 1073 1022  561 1274 1238 1363 1360 1156 1454 1431 1137  396 1238

12    1094 1412 1369 1351 1278 1316 1053 1086 1030  565 1280 1240 1368 1370 1164 1476 1451 1151  398 1240

11    1086 1414 1369 1351 1278 1317 1047 1089 1033  567 1280 1238 1368 1372 1164 1484 1461 1158  398 1238

10    1077 1412 1366 1349 1276 1315 1040 1088 1033  566 1277 1235 1366 1370 1161 1487 1466 1161  397 1235

9    1069 1409 1363 1346 1273 1311 1033 1085 1032  565 1273 1231 1363 1368 1157 1487 1468 1163  395 1231

8    1062 1406 1360 1343 1269 1308 1027 1082 1029  562 1270 1227 1360 1365 1153 1486 1469 1162  393 1227

7    1055 1402 1356 1340 1265 1303 1019 1076 1024  558 1266 1223 1356 1362 1147 1482 1465 1157  390 1223

6    1046 1395 1350 1333 1259 1294 1008 1067 1013  551 1259 1217 1350 1354 1138 1471 1454 1146  384 1217

5    1028 1380 1335 1318 1245 1277  988 1050  994  538 1245 1204 1335 1338 1122 1446 1428 1121  375 1204

4     993 1343 1301 1285 1214 1241  949 1017  957  515 1215 1176 1301 1301 1090 1394 1372 1072  359 1176

3     925 1265 1227 1211 1147 1166  878  954  889  474 1149 1114 1227 1224 1027 1292 1264  980  332 1114

2     797 1107 1075 1059 1010 1019  752  837  767  404 1013  984 1073 1068  905 1103 1067  818  285  985

1     607  818  787  774  748  755  570  633  558  289  753  733  784  777  682  787  743  561  208  733

21   22   23   24   25   26   27   28   29   30   31   32   33   34   35   36   37   38   39   40

20     657  599  560  514  510  497  310  644  599    0  564  598    0  315  617  561  565  622  591  449

19     934  841  798  713  734  771  478  922  841  871  804  863  860  501  874  799  806  896  869  707

18    1123 1002  958  853  890  977  607 1111 1002 1026  964 1054 1051  619 1060  959  965 1090 1074  893

17    1234 1094 1051  937  982 1113  693 1221 1094 1128 1056 1172 1190  690 1174 1052 1058 1210 1203 1012

16    1299 1148 1108  992 1042 1202  750 1286 1148 1188 1111 1246 1279  734 1247 1109 1112 1282 1283 1086

15    1338 1181 1143 1026 1072 1260  786 1325 1181 1224 1143 1292 1336  760 1293 1143 1144 1327 1332 1132

14    1362 1201 1170 1058 1104 1302  810 1350 1201 1247 1164 1323 1373  776 1335 1171 1165 1354 1363 1160

13    1376 1212 1185 1075 1119 1328  825 1363 1212 1260 1174 1341 1396  785 1360 1185 1175 1369 1381 1177

12    1381 1216 1189 1080 1123 1344  833 1368 1216 1264 1177 1351 1410  789 1370 1190 1178 1377 1392 1187

11    1381 1215 1189 1080 1124 1352  837 1368 1215 1264 1176 1355 1418  790 1371 1189 1177 1380 1398 1192

10    1380 1212 1186 1077 1123 1357  839 1366 1212 1262 1174 1356 1423  790 1370 1186 1175 1381 1402 1196

9    1377 1208 1182 1074 1121 1360  839 1363 1208 1259 1171 1357 1426  789 1368 1182 1172 1382 1404 1197

8    1375 1204 1178 1070 1119 1360  837 1360 1204 1256 1168 1356 1427  786 1365 1179 1169 1381 1405 1197

7    1372 1200 1173 1065 1115 1357  833 1356 1200 1251 1163 1352 1424  782 1361 1174 1164 1378 1403 1194

6    1365 1193 1166 1056 1106 1346  823 1349 1193 1243 1155 1344 1414  774 1354 1166 1156 1370 1394 1184

5    1350 1178 1151 1040 1088 1320  803 1334 1178 1227 1139 1323 1388  759 1337 1151 1140 1350 1372 1160

4    1315 1149 1120 1009 1053 1265  765 1301 1149 1193 1107 1280 1334  729 1301 1121 1108 1307 1323 1111

3    1239 1086 1057  951  986 1160  696 1227 1086 1123 1043 1194 1227  675 1224 1058 1044 1220 1227 1018

2    1081  958  931  839  860  972  576 1073  958  980  916 1029 1033  579 1068  931  917 1053 1046  852

1     787  711  690  631  635  669  391  783  712  716  678  739  715  417  777  691  679  757  739  585

41   42   43   44   45   46   47   48   49   50   51   52   53   54   55   56   57   58   59

20     196  480  519  599  591  505  266  507  512    0  448  263  548  497  315  195  449  310  169

19     284  669  722  866  870  757  383  743  735  861  706  376  808  772  501  283  657  478  256

18     342  840  864 1057 1075  950  464  973  892 1052  892  455 1019  978  618  341  829  607  312

17     377  932  946 1175 1204 1075  512 1114  984 1191 1011  503 1162 1113  690  375  945  694  347

16     397 1049 1000 1249 1284 1153  541 1282 1044 1280 1085  532 1263 1202  733  395 1023  750  370

15     408 1068 1028 1294 1333 1201  554 1327 1073 1336 1131  549 1330 1261  760  407 1075  786  384

14     413 1119 1060 1325 1364 1231  563 1396 1105 1373 1160  557 1391 1302  776  413 1113  810  393

13     416 1156 1077 1343 1382 1248  565 1454 1120 1397 1177  561 1430 1328  785  415 1137  825  398

12     416 1165 1081 1353 1393 1259  564 1476 1123 1410 1187  561 1451 1344  789  415 1151  833  400

11     415 1165 1080 1357 1399 1265  563 1484 1124 1418 1192  561 1460 1352  791  415 1158  837  401

10     414 1162 1077 1358 1403 1269  561 1487 1123 1423 1196  560 1465 1357  790  413 1162  839  400

9     412 1158 1074 1359 1405 1271  560 1487 1122 1426 1197  558 1468 1360  789  412 1163  839  398

8     410 1154 1070 1358 1406 1272  558 1486 1120 1428 1197  556 1468 1361  787  410 1162  838  396

7     407 1149 1065 1355 1404 1269  554 1482 1115 1425 1194  552 1465 1358  782  407 1158  833  393

6     402 1140 1057 1346 1396 1259  548 1472 1107 1415 1184  545 1454 1347  774  402 1146  824  388

5     394 1124 1041 1325 1373 1234  536 1447 1089 1389 1160  534 1428 1320  759  393 1122  804  378

4     378 1092 1011 1282 1325 1183  514 1395 1054 1335 1111  512 1372 1265  729  378 1072  766  362

3     351 1029  953 1196 1228 1085  476 1292  987 1228 1018  474 1264 1161  675  351  981  696  335

2     304  907  841 1031 1047  908  407 1104  860 1034  852  406 1067  972  579  304  819  577  287

1     222  684  632  740  740  624  293  788  636  716  585  292  743  669  417  222  561  391  209

Tab. 2: Axial Burn-up Distribution, [MWd/kg]

(Calculated by MOBY-DICK, accuracy 7 %)

20 - bottom of assembly

1 - top of assembly

1    2    3    4    5    6    7    8    9   10   11   12   13   14   15   16   17   18   19   20

20    16.7  9.0 10.6 10.9 14.8 10.4 13.5 22.3 17.4 14.8 15.3 16.8 10.1  8.3 17.6  3.0  2.9  2.1 22.3 16.8

19    23.3 12.9 15.0 15.4 20.9 14.7 19.0 31.1 24.1 20.8 21.4 23.5 14.4 11.9 24.3  4.4  4.2  3.2 30.7 23.5

18    27.0 15.2 17.6 18.2 24.4 17.3 22.2 36.3 28.1 24.3 24.9 27.4 17.0 14.1 28.1  5.2  5.1  3.9 35.4 27.4

17    28.9 16.5 19.0 19.6 26.3 18.7 23.9 39.1 30.2 26.2 26.7 29.5 18.4 15.4 30.2  5.8  5.7  4.4 37.8 29.5

16    29.9 17.2 19.7 20.4 27.3 19.4 24.7 40.6 31.2 27.1 27.6 30.6 19.2 16.0 31.2  6.1  6.0  4.6 38.9 30.6

15    32.7 17.5 20.0 20.7 27.8 19.7 27.4 41.3 31.7 27.6 28.0 31.1 19.5 16.4 31.7  6.3  6.2  4.8 39.4 31.1

14    33.8 17.7 20.2 20.9 27.9 19.9 28.3 41.5 31.8 27.7 28.2 31.2 19.6 16.5 31.9  6.4  6.3  4.9 39.5 31.2

13    34.4 17.7 20.2 20.9 28.0 19.9 28.9 41.6 31.8 27.8 28.2 31.3 19.7 16.5 31.9  6.4  6.3  4.9 39.5 31.3

12    34.7 17.6 20.1 20.8 27.9 19.8 29.2 41.4 31.7 27.7 28.2 31.2 19.6 16.5 31.9  6.4  6.3  4.9 39.3 31.2

11    34.8 17.6 20.0 20.7 27.8 19.7 29.4 41.2 31.5 27.6 28.0 31.0 19.5 16.4 31.7  6.4  6.3  4.9 39.1 31.0

10    34.8 17.4 19.8 20.5 27.6 19.5 29.3 40.9 31.2 27.4 27.9 30.8 19.3 16.3 31.5  6.3  6.2  4.8 38.9 30.8

9    34.6 17.2 19.5 20.3 27.3 19.2 29.2 40.4 30.8 27.1 27.6 30.5 19.1 16.1 31.0  6.2  6.1  4.7 38.5 30.5

8    34.3 16.8 19.1 20.0 26.9 18.8 28.9 39.8 30.1 26.8 27.2 30.1 18.7 15.8 30.2  6.0  5.9  4.6 37.9 30.1

7    33.8 16.3 18.5 19.6 26.4 18.1 28.5 38.8 29.5 26.3 26.6 29.5 18.3 15.4 29.3  5.7  5.6  4.4 37.1 29.5

6    33.2 15.6 17.8 19.0 25.6 17.3 28.0 37.6 28.8 25.7 25.8 28.7 17.7 14.9 28.4  5.3  5.3  4.2 36.2 28.7

5    32.2 14.9 16.9 18.2 24.6 16.5 27.1 36.1 26.8 24.7 24.8 27.6 16.9 14.2 26.4  5.0  4.9  3.9 34.8 27.6

4    30.7 13.5 15.7 17.0 23.1 15.0 25.8 33.5 24.9 23.2 23.2 25.9 15.7 13.2 24.3  4.2  4.4  3.6 32.8 25.9

3    28.2 11.9 13.9 15.1 20.7 13.2 23.6 30.0 21.8 20.9 20.8 23.2 13.9 11.7 21.2  3.6  3.8  3.0 29.6 23.2

2    24.3  9.4 11.2 12.5 16.9 10.5 20.2 24.5 17.8 17.4 17.0 19.0 11.2  9.3 17.2  2.7  2.9  2.4 24.5 19.0

1     0.0  6.6  7.8  0.0 11.7  7.3  0.0 17.5 12.6  0.0 11.8 13.1  7.5  6.0 12.2  1.8  1.9  1.6 17.6 13.1

21   22   23   24   25   26   27   28   29   30   31   32   33   34   35   36   37   38   39   40

20     9.0 16.3 15.0 22.4 21.7  2.6  1.5 10.1 16.3 10.6 16.2  8.7  2.9 16.0  8.3 15.0 16.2  8.8  7.1  2.3

19    12.8 22.9 21.0 30.9 29.8  3.8  2.2 14.4 22.9 15.0 22.7 12.5  4.3 22.5 11.9 21.0 22.7 12.6 10.4  3.4

18    15.1 26.6 24.5 35.7 34.6  4.7  2.7 17.0 26.6 17.7 26.5 14.8  5.3 26.4 14.1 24.5 26.5 15.0 12.5  4.1

17    16.3 28.6 26.5 38.1 37.1  5.2  3.1 18.4 28.6 19.1 28.5 16.1  5.9 28.4 15.3 26.4 28.5 16.3 13.7  4.6

16    17.0 29.6 27.4 39.3 38.4  5.5  3.3 19.1 29.5 19.9 29.5 16.8  6.2 29.5 16.0 27.4 29.5 17.0 14.4  4.9

15    17.3 30.0 27.9 39.8 39.0  5.7  3.4 19.5 30.0 20.3 30.0 17.2  6.4 30.0 16.3 27.9 30.0 17.4 14.7  5.0

14    17.5 30.1 28.1 40.0 39.3  5.8  3.5 19.6 30.1 20.4 30.1 17.4  6.5 30.2 16.5 28.1 30.1 17.5 14.9  5.1

13    17.5 30.2 28.1 40.0 39.3  5.8  3.5 19.6 30.1 20.4 30.2 17.4  6.5 30.2 16.5 28.1 30.2 17.6 14.9  5.1

12    17.4 30.1 28.0 39.9 39.2  5.8  3.5 19.6 30.1 20.4 30.1 17.3  6.5 30.1 16.5 28.0 30.1 17.5 14.9  5.1

11    17.4 29.9 27.9 39.7 39.0  5.8  3.5 19.5 29.9 20.2 29.9 17.2  6.5 29.9 16.4 27.9 29.9 17.4 14.8  5.1

10    17.3 29.7 27.7 39.4 38.7  5.7  3.5 19.3 29.7 20.1 29.7 17.1  6.4 29.7 16.3 27.7 29.7 17.2 14.6  5.0

9    17.1 29.5 27.4 39.0 38.1  5.6  3.4 19.0 29.5 19.8 29.4 16.9  6.3 29.4 16.1 27.4 29.4 17.0 14.4  5.0

8    16.9 29.1 26.9 38.4 37.1  5.5  3.3 18.7 29.1 19.5 28.9 16.6  6.1 29.0 15.8 26.9 28.9 16.7 14.2  4.9

7    16.5 28.6 26.3 37.6 36.1  5.3  3.2 18.2 28.6 19.1 28.2 16.3  5.9 28.4 15.4 26.2 28.2 16.2 13.8  4.7

6    16.1 27.9 25.5 36.5 35.2  5.0  3.1 17.6 27.9 18.5 27.4 15.8  5.7 27.6 14.9 25.5 27.4 15.7 13.3  4.5

5    15.5 26.8 24.4 35.1 32.4  4.7  2.9 16.8 26.8 17.7 26.3 15.1  5.3 26.5 14.2 24.4 26.3 14.9 12.7  4.2

4    14.5 25.2 22.8 33.0 30.1  4.2  2.6 15.7 25.3 16.5 24.6 14.0  4.8 24.9 13.2 22.8 24.7 13.8 11.7  3.9

3    12.9 22.7 20.3 29.7 26.1  3.6  2.2 13.9 22.7 14.7 22.1 12.4  4.2 22.2 11.6 20.3 22.1 12.2 10.3  3.3

2    10.5 18.6 16.6 24.6 21.4  2.8  1.7 11.1 18.6 12.2 18.1  9.9  3.3 18.1  9.3 16.6 18.1  9.8  8.1  2.6

1     7.1 12.8 11.6 17.5 15.1  1.8  1.1  7.5 12.8  0.0 12.7  6.5  0.0 12.4  6.0 11.6 12.8  6.8  5.4  1.6

41   42   43   44   45   46   47   48   49   50   51   52   53   54   55   56   57   58   59

20    20.4 17.3 22.4  8.7  7.1  2.4 16.1  3.0 21.7  2.9  2.3 16.1  2.9  2.6 16.0 20.4  2.1  1.5 21.8

19    28.4 24.0 30.8 12.5 10.4  3.6 22.2  4.4 29.8  4.4  3.4 22.5  4.2  3.8 22.5 28.5  3.2  2.2 30.0

18    33.1 27.9 35.5 14.8 12.5  4.4 25.9  5.2 34.6  5.3  4.1 26.2  5.1  4.7 26.4 33.1  3.9  2.7 34.6

17    35.5 30.0 38.0 16.1 13.7  4.9 27.8  5.8 37.1  5.9  4.6 28.2  5.7  5.2 28.4 35.6  4.4  3.1 37.0

16    36.8 31.1 39.2 16.8 14.4  5.2 28.8  6.1 38.4  6.2  4.9 29.1  6.0  5.6 29.5 36.8  4.6  3.3 38.1

15    37.3 31.6 39.8 17.2 14.7  5.4 29.2  6.3 39.0  6.4  5.0 29.6  6.2  5.7 30.0 37.4  4.8  3.4 38.6

14    37.5 31.8 40.0 17.3 14.9  5.5 29.4  6.4 39.3  6.5  5.1 29.7  6.3  5.8 30.2 37.6  4.9  3.5 38.7

13    37.5 31.8 40.0 17.4 14.9  5.5 29.4  6.4 39.3  6.5  5.1 29.7  6.3  5.9 30.2 37.6  4.9  3.5 38.7

12    37.4 31.7 39.9 17.3 14.9  5.5 29.3  6.4 39.2  6.5  5.1 29.6  6.3  5.8 30.1 37.5  4.9  3.5 38.6

11    37.2 31.6 39.7 17.2 14.8  5.4 29.1  6.4 39.0  6.5  5.1 29.4  6.3  5.8 29.9 37.3  4.9  3.5 38.4

10    37.0 31.3 39.5 17.1 14.6  5.4 28.9  6.3 38.7  6.4  5.0 29.2  6.2  5.7 29.7 37.0  4.8  3.5 38.2

9    36.6 30.9 39.0 16.9 14.4  5.3 28.5  6.2 38.1  6.3  5.0 28.8  6.1  5.6 29.4 36.7  4.7  3.4 37.8

8    36.1 30.2 38.2 16.6 14.2  5.2 27.7  6.0 37.1  6.1  4.9 28.4  5.9  5.5 28.9 36.1  4.6  3.3 37.4

7    35.4 29.4 37.4 16.3 13.8  5.0 27.0  5.7 36.1  5.9  4.7 27.8  5.6  5.3 28.4 35.5  4.4  3.2 36.7

6    34.5 28.6 36.5 15.8 13.3  4.8 26.3  5.3 35.2  5.7  4.5 27.0  5.3  5.0 27.6 34.6  4.2  3.1 35.9

5    33.2 26.7 34.4 15.1 12.7  4.5 24.4  5.0 32.4  5.3  4.2 26.0  4.9  4.7 26.5 33.3  3.9  2.9 34.7

4    31.2 24.6 32.2 14.0 11.7  4.1 22.6  4.2 30.1  4.8  3.9 24.3  4.4  4.2 24.9 31.3  3.6  2.6 32.7

3    28.1 21.5 28.5 12.4 10.3  3.6 19.8  3.6 26.2  4.2  3.3 21.8  3.8  3.6 22.2 28.1  3.0  2.2 29.7

2    23.1 17.4 23.5  9.9  8.1  2.8 16.2  2.7 21.4  3.3  2.6 17.9  2.9  2.8 18.1 23.1  2.4  1.7 24.7

1    16.0 12.1 16.7  6.5  5.4  1.8 11.4  1.8 15.1  0.0  1.6 12.4  1.9  1.8 12.4 16.0  1.6  1.1 17.6

Tab. 3: Measured Data from the Tests

|  | Time | Power | T. rise | Bank 6 | Tin | BAC |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | [min] | [%] | [°C] | [cm] | [°C] | [g/kg] |  |  |  |
|  | TEST No. 1 |  |  |  |  |  |  |  |  |
|  | 0 | 100.0 | 30.2 | 191 | 267.2 | 3.05 | BAC - actual (measured value) |
|  | 17 | 79.0 | 24.2 | 141 | 265.5 |  |  |  |  |
|  | 30 | 79.0 | 24.1 | 142 | 265.1 |  |  |  |  |
|  | 41 | 79.3 | 24.2 | 143 | 265.0 |  |  |  |  |
|  | 50 | 79.3 | 24.2 | 145 | 265.0 |  |  |  |  |
|  | 62 | 79.0 | 24.1 | 146 | 265.0 |  |  |  |  |
|  | 75 | 79.1 | 24.1 | 148 | 265.1 |  |  |  |  |
|  | 85 | 79.1 | 24.1 | 150 | 265.1 |  |  |  |  |
|  | 100 | 79.1 | 24.2 | 151 | 265.1 |  |  |  |  |
|  | 115 | 79.2 | 24.2 | 154 | 265.0 |  |  |  |  |
|  | 130 | 79.2 | 24.2 | 155 | 265.1 |  |  |  |  |
|  | 145 | 79.2 | 24.2 | 157 | 265.1 |  |  |  |  |
|  | 160 | 79.2 | 24.2 | 158 | 265.0 |  |  |  |  |
|  | 162 | 82.1 |  | 166 | 264.7 |  |  |  |  |
|  | 165 |  |  | 170 |  |  |  |  |  |
|  | 170 | 88.8 | 27.0 | 182 | 265.3 |  |  |  |  |
|  | 175 | 93.6 | 28.4 | 195 | 265.8 |  |  |  |  |
|  | 179 | 98.6 | 29.8 | 210 | 266.3 |  |  |  |  |
|  | 180 |  |  | 216 |  |  |  |  |  |
|  | 185 | 99.7 | 30.2 | 216 | 267.2 |  |  |  |  |
|  | 195 | 100.0 | 30.2 | 212 | 267.1 |  |  |  |  |
|  | 205 | 100.2 | 30.3 | 211 | 267.3 |  |  |  |  |
|  | 220 | 100.0 | 30.2 | 208 | 267.2 |  |  |  |  |
|  | 235 | 99.8 | 30.2 | 205 | 267.2 |  |  |  |  |
|  | 250 | 99.6 | 30.1 | 201 | 267.1 |  |  |  |  |
|  | 265 | 99.4 | 30.1 | 199 | 267.1 | 2.90 | BAC - actual (measured value) |
|  | 280 | 99.5 | 30.1 | 198 | 267.1 |  |  |  |  |
|  | 295 | 99.3 | 30.0 | 195 | 267.1 |  |  |  |  |
|  | 310 | 98.9 | 29.9 | 193 | 267.1 |  |  |  |  |
|  | 318 | 99.6 | 30.1 | 195 | 267.2 |  |  |  |  |
|  | 325 | 99.8 | 30.2 | 195 | 267.2 |  |  |  |  |
|  | TEST No. 2 |  |  |  |  |  |  |  |  |
|  | 340 | 100.2 | 30.3 | 195 | 267.3 |  |  |  |  |
|  | 348 | 90.8 | 27.6 | 171 | 266.8 |  |  |  |  |
|  | 355 | 91.1 | 27.7 | 171 | 266.4 |  |  |  |  |
|  | 360 | 98.1 | 29.7 | 187 | 266.3 |  |  |  |  |
|  | 363 | 98.9 | 29.9 | 190 | 266.6 |  |  |  |  |
|  | 370 | 93.7 | 28.4 | 178 | 267.2 |  |  |  |  |
|  | 371 | 92.7 | 28.1 | 175 | 267.0 |  |  |  |  |
|  | 373 | 89.8 | 27.3 | 167 | 266.7 |  |  |  |  |
|  | 376 | 92.6 | 28.1 | 175 | 265.8 |  |  |  |  |
|  | 378 | 94.6 | 28.7 | 179 | 266.0 |  |  |  |  |
|  | 383 | 99.7 | 30.1 | 190 | 266.5 |  |  |  |  |
|  | 386 | 99.3 | 30.0 | 192 | 267.4 |  |  |  |  |
|  | 394 | 98.9 | 29.9 | 188 | 266.7 |  |  |  |  |
|  | TEST No. 3 |  |  |  |  |  |  |  |  |
|  | 398 | 99.7 | 30.1 | 188 | 266.3 |  |  |  |  |
|  | 405 | 95.3 | 28.9 | 183 | 267.6 |  |  |  |  |
|  | 406 | 93.7 | 28.4 | 179 | 267.7 |  |  |  |  |
|  | 407 | 91.7 | 27.8 | 175 | 267.7 | 2.90 | BAC - actual (measured value) |
|  | 413 | 94.1 | 28.5 | 180 | 266.8 |  |  |  |  |
|  | 416 | 96.8 | 29.3 | 184 | 266.9 |  |  |  |  |
|  | 420 | 99.3 | 30.0 | 184 | 265.8 |  |  |  |  |
|  | 426 | 92.6 | 28.1 | 177 | 267.9 |  |  |  |  |
|  | 429 | 90.6 | 27.5 | 177 | 268.4 |  |  |  |  |
|  | 433 | 93.6 | 28.4 | 177 | 267.0 |  |  |  |  |
|  | 435 | 94.6 | 28.8 | 181 | 266.5 |  |  |  |  |
|  | 439 | 99.1 | 30.0 | 187 | 265.9 |  |  |  |  |
|  | 441 | 100.0 | 30.2 | 187 | 266.1 |  |  |  |  |
|  | 447 | 99.5 | 30.0 | 187 | 266.4 |  |  |  |  |
|  | TEST No. 4 |  |  |  |  |  |  |  |  |
|  | 450 | 99.4 | 30.0 | 187 | 266.5 |  |  |  |  |
|  | 460 | 93.6 | 28.4 | 179 | 267.8 |  |  |  |  |
|  | 464 | 90.7 | 27.6 | 175 | 268.1 |  |  |  |  |
|  | 475 | 90.2 | 27.4 | 175 | 268.1 |  |  |  |  |
|  | 488 | 83.1 | 25.4 | 163 | 268.6 |  |  |  |  |
|  | 500 | 82.5 | 25.2 | 163 | 268.6 |  |  |  |  |
|  | 509 | 77.6 | 23.7 | 153 | 268.6 |  |  |  |  |
|  | 514 | 75.8 | 23.2 | 149 | 268.4 |  |  |  |  |
|  | 525 | 74.9 | 23.0 | 150 | 268.5 |  |  |  |  |
|  | 536 | 68.1 | 21.1 | 134 | 268.2 | +0.10 | BAC - change |
|  | 538 | 68.1 | 21.0 | 134 | 268.1 |  |  |  |  |
|  | 550 | 67.7 | 20.8 | 137 | 267.8 |  |  |  |  |
|  | 564 | 61.1 | 18.9 | 128 | 267.2 |  |  |  |  |
|  | 575 | 60.0 | 18.5 | 132 | 267.1 |  |  |  |  |
|  | 582 | 56.8 | 17.6 | 125 | 266.9 |  |  |  |  |
|  | 584 | 56.3 | 17.4 | 125 | 266.7 |  |  |  |  |
|  | 594 | 56.0 | 17.3 | 127 | 266.7 |  |  |  |  |
|  | 610 | 55.8 | 17.3 | 132 | 266.7 |  |  |  |  |
|  | 625 | 55.8 | 17.3 | 138 | 266.7 |  |  |  |  |
|  | 630 | 55.8 | 17.3 | 138 | 266.7 |  |  |  |  |
|  | 640 | 60.4 | 18.6 | 150 | 266.6 |  |  |  |  |
|  | 643 | 62.0 | 19.1 | 156 | 266.8 |  |  |  |  |
|  | 645 | 62.7 | 19.3 | 158 | 266.8 |  |  |  |  |
|  | 652 | 62.8 | 19.4 | 160 | 267.4 |  |  |  |  |
|  | 655 | 62.9 | 19.4 | 160 | 267.4 |  |  |  |  |
|  | 658 | 64.0 | 19.7 | 164 | 267.0 |  |  |  |  |
|  | 663 | 66.3 | 20.4 | 170 | 267.2 |  |  |  |  |
|  | 667 | 68.6 | 21.1 | 174 | 267.4 |  |  |  |  |
|  | 670 | 70.4 | 21.6 | 178 | 267.6 |  |  |  |  |
|  | 680 | 69.9 | 31.5 | 178 | 268.0 |  |  |  |  |
|  | 690 | 69.9 | 21.5 | 178 | 268.0 |  |  |  |  |
|  | 696 | 72.2 | 22.1 | 181 | 267.7 |  |  |  |  |
|  | 700 | 73.8 | 22.6 | 185 | 267.9 |  |  |  |  |
|  | 702 | 76.2 | 23.3 | 192 | 268.1 |  |  |  |  |
|  | 707 | 77.6 | 23.7 | 196 | 268.4 |  |  |  |  |
|  | 710 | 78.8 | 24.1 | 200 | 268.7 |  |  |  |  |
|  | 720 | 79.1 | 24.2 | 200 | 268.9 |  |  |  |  |
|  | 726 | 81.1 | 24.7 | 203 | 268.1 |  |  |  |  |
|  | 728 | 83.0 | 25.3 | 206 | 268.5 |  |  |  |  |
|  | 736 | 85.2 | 25.9 | 210 | 267.8 |  |  |  |  |
|  | 746 | 87.2 | 26.5 | 210 | 268.2 |  |  |  |  |
|  | 752 | 88.8 | 27.1 | 210 | 267.6 |  |  |  |  |
|  | 754 | 90.6 | 27.5 | 214 | 267.1 |  |  |  |  |
|  | 760 | 93.2 | 25.8 | 214 | 266.8 | 3.05 | BAC - actual (measured value) |
|  | 762 | 95.3 | 28.9 | 216 | 266.6 |  |  |  |  |
|  | 772 | 95.8 | 29.0 | 216 | 266.9 |  |  |  |  |
|  | 776 | 97.0 | 29.4 | 216 | 266.6 |  |  |  |  |
|  | 780 | 99.3 | 30.0 | 218 | 265.8 |  |  |  |  |
|  | 781 | 100.0 | 30.2 | 218 | 265.8 |  |  |  |  |
|  | 786 | 98.6 | 29.8 | 220 | 267.0 |  |  |  |  |
|  | 787 | 98.9 | 29.9 | 221 | 267.1 |  |  |  |  |
|  | 790 | 99.5 | 30.0 | 221 | 267.1 |  |  |  |  |
|  | 803 | 99.5 | 30.0 | 215 | 267.1 |  |  |  |  |
|  | 808 | 99.2 | 30.0 | 213 | 267.1 |  |  |  |  |
|  | 820 | 99.8 | 30.1 | 210 | 267.1 |  |  |  |  |
|  | 826 | 99.6 | 30.1 | 209 | 267.1 |  |  |  |  |
|  | TEST No. 5 |  |  |  |  |  |  |  |  |
|  | 830 | 99.6 | 30.1 | 208 | 267.2 |  |  |  |  |
|  | 833 | 97.6 | 29.5 | 204 | 267.5 |  |  |  |  |
|  | 835 | 96.2 | 29.1 | 200 | 267.3 |  |  |  |  |
|  | 838 | 96.0 | 28.9 | 196 | 267.2 | 3.05 | BAC - actual (measured value) |
|  | 840 | 93.9 | 28.4 | 192 | 267.0 |  |  |  |  |
|  | 844 | 91.7 | 27.7 | 185 | 266.8 |  |  |  |  |
|  | 850 | 91.9 | 27.9 | 185 | 266.2 |  |  |  |  |
|  | 855 | 91.5 | 27.8 | 182 | 266.2 |  |  |  |  |
|  | 857 | 89.1 | 26.9 | 176 | 266.5 |  |  |  |  |
|  | 862 | 86.1 | 26.2 | 170 | 266.1 |  |  |  |  |
|  | 865 | 83.4 | 25.4 | 165 | 265.9 |  |  |  |  |
|  | 870 | 83.7 | 25.5 | 163 | 265.4 |  |  |  |  |
|  | 877 | 83.7 | 25.5 | 163 | 265.4 |  |  |  |  |
|  | 881 | 80.6 | 24.6 | 155 | 265.6 |  |  |  |  |
|  | 886 | 78.5 | 24.0 | 150 | 265.4 | +0.10 | BAC - change |
|  | 888 | 77.3 | 23.6 | 147 | 264.8 | 3.15 | BAC - actual (measured value) |
|  | 896 | 76.7 | 23.5 | 145 | 264.7 |  |  |  |  |
|  | 899 | 74.1 | 22.7 | 140 | 265.0 |  |  |  |  |
|  | 905 | 72.6 | 22.3 | 137 | 264.7 |  |  |  |  |
|  | 912 | 70.6 | 21.7 | 137 | 264.0 |  |  |  |  |
|  | 915 | 69.6 | 21.4 | 137 | 264.1 |  |  |  |  |
|  | 924 | 69.6 | 21.4 | 137 | 263.9 |  |  |  |  |
|  | 930 | 67.7 | 20.8 | 134 | 264.4 |  |  |  |  |
|  | 932 | 65.8 | 20.2 | 131 | 264.1 |  |  |  |  |
|  | 934 | 64.7 | 19.9 | 128 | 264.1 |  |  |  |  |
|  | 935 | 64.0 | 19.7 | 125 | 264.1 |  |  |  |  |
|  | 946 | 63.5 | 19.6 | 126 | 263.4 |  |  |  |  |
|  | 951 | 63.3 | 19.5 | 125 | 263.4 |  |  |  |  |
|  | 955 | 62.6 | 19.3 | 125 | 263.4 |  |  |  |  |
|  | 965 | 61.4 | 18.9 | 125 | 263.5 |  |  |  |  |
|  | 972 | 59.3 | 18.2 | 125 | 263.2 |  |  |  |  |
|  | 980 | 58.3 | 18.0 | 125 | 263.2 |  |  |  |  |
|  | 990 | 57.0 | 17.6 | 125 | 263.1 |  |  |  |  |
|  | 994 | 56.8 | 17.6 | 125 | 263.0 |  |  |  |  |
|  | 1000 | 56.0 | 17.3 | 125 | 263.0 |  |  |  |  |
|  | 1005 | 55.7 | 17.2 | 125 | 263.0 |  |  |  |  |
|  | 1015 | 54.7 | 17.0 | 125 | 262.8 |  |  |  |  |
|  | 1024 | 54.7 | 17.0 | 127 | 262.8 |  |  |  |  |
|  | 1028 | 55.0 | 17.0 | 128 | 262.7 |  |  |  |  |
|  | 1038 | 55.0 | 17.0 | 130 | 262.7 |  |  |  |  |
|  | 1045 | 55.2 | 17.0 | 131 | 262.7 | 3.15 | BAC - actual (measured value) |
|  | 1047 | 56.8 | 17.5 | 134 | 262.2 |  |  |  |  |
|  | 1051 | 58.6 | 18.0 | 140 | 262.4 |  |  |  |  |
|  | 1055 | 60.9 | 18.8 | 146 | 262.6 |  |  |  |  |
|  | 1058 | 62.2 | 19.2 | 148 | 262.7 |  |  |  |  |
|  | 1063 | 61.8 | 19.0 | 150 | 263.4 |  |  |  |  |
|  | 1068 | 61.8 | 19.0 | 150 | 263.4 |  |  |  |  |
|  | 1071 | 63.2 | 19.5 | 154 | 262.9 |  |  |  |  |
|  | 1073 | 65.2 | 20.0 | 157 | 263.0 |  |  |  |  |
|  | 1075 | 66.3 | 20.4 | 160 | 263.1 |  |  |  |  |
|  | 1079 | 68.4 | 21.0 | 167 | 263.3 |  |  |  |  |
|  | 1084 | 71.6 | 22.0 | 174 | 263.6 |  |  |  |  |
|  | 1094 | 71.6 | 22.0 | 174 | 264.3 |  |  |  |  |
|  | 1098 | 73.1 | 22.5 | 177 | 263.9 |  |  |  |  |
|  | 1101 | 74.4 | 22.8 | 180 | 263.9 |  |  |  |  |
|  | 1105 | 77.1 | 23.8 | 186 | 264.2 |  |  |  |  |
|  | 1110 | 77.9 | 23.8 | 186 | 265.0 |  |  |  |  |
|  | 1115 | 78.1 | 23.9 | 186 | 265.0 |  |  |  |  |
|  | 1119 | 79.2 | 24.4 | 190 | 264.6 |  |  |  |  |
|  | 1120 | 83.7 | 25.5 | 199 | 265.0 |  |  |  |  |
|  | 1123 | 81.1 | 24.4 | 194 | 265.5 |  |  |  |  |
|  | 1126 | 83.2 | 25.4 | 197 | 265.0 |  |  |  |  |
|  | 1131 | 84.2 | 25.7 | 200 | 265.1 |  |  |  |  |
|  | 1132 | 85.6 | 26.0 | 200 | 265.4 |  |  |  |  |
|  | 1136 | 85.6 | 26.1 | 200 | 265.7 |  |  |  |  |
|  | 1142 | 85.6 | 26.1 | 200 | 265.8 |  |  |  |  |
|  | 1143 | 86.6 | 26.4 | 202 | 265.9 |  |  |  |  |
|  | 1145 | 87.2 | 26.5 | 204 | 265.9 |  |  |  |  |
|  | 1146 | 87.8 | 26.7 | 205 | 266.0 |  |  |  |  |
|  | 1150 | 88.5 | 26.9 | 205 | 266.0 |  |  |  |  |
|  | 1160 | 88.4 | 26.9 | 202 | 266.0 |  |  |  |  |
|  | 1169 | 88.3 | 26.8 | 199 | 266.0 | 3.15 | BAC - actual (measured value) |
|  | 1174 | 87.8 | 26.7 | 197 | 266.0 |  |  |  |  |
|  | TEST No. 6 |  |  |  |  |  |  |  |  |
|  | 1179 | 87.8 | 26.7 | 196 | 266.0 |  |  |  |  |
|  | 1189 | 87.7 | 26.7 | 194 | 266.0 |  |  |  |  |
|  | 1200 | 87.4 | 26.6 | 191 | 265.9 |  |  |  |  |
|  | 1206 | 87.4 | 26.6 | 189 | 265.9 |  |  |  |  |
|  | 1208 | 80.5 | 24.4 | 169 | 265.8 |  |  |  |  |
|  | 1209 | 83.7 | 25.5 | 181 | 264.9 |  |  |  |  |
|  | 1211 | 84.2 | 25.6 | 175 | 265.5 |  |  |  |  |
|  | 1213 | 81.7 | 24.8 | 173 | 264.3 |  |  |  |  |
|  | 1217 | 81.3 | 24.8 | 173 | 265.1 |  |  |  |  |
|  | 1223 | 81.3 | 25.6 | 173 | 265.5 |  | Main pump No 6: switch off |  |  |
|  | 1228 | 75.3 | 25.0 | 173 | 265.1 |  |  |  |  |
|  | 1230 | 76.6 | 25.6 | 180 | 265.2 |  |  |  |  |
|  | 1233 | 78.0 | 26.0 | 182 | 265.6 |  |  |  |  |
|  | 1247 | 78.5 | 26.1 | 182 | 265.8 |  |  |  |  |
|  | 1261 | 78.0 | 25.9 | 182 | 266.3 |  |  |  |  |
|  | 1276 | 78.4 | 26.0 | 182 | 266.3 |  |  |  |  |
|  | 1290 | 78.3 | 26.0 | 181 | 266.2 |  |  |  |  |
|  | 1303 | 78.4 | 26.0 | 181 | 266.3 |  | Main pump No 6: switch on |  |  |
|  | 1305 | 78.0 | 23.4 | 163 | 265.2 |  |  |  |  |
|  | 1307 | 78.3 | 23.9 | 162 | 265.2 |  |  |  |  |
|  | 1312 | 77.9 | 23.8 | 160 | 265.0 |  |  |  |  |
|  | 1321 | 78.5 | 24.0 | 165 | 264.8 |  |  |  |  |
|  | 1325 | 80.2 | 24.5 | 167 | 264.9 |  |  |  |  |
|  | 1327 | 82.2 | 25.1 | 171 | 264.9 |  |  |  |  |
|  | 1330 | 83.2 | 25.4 | 174 | 265.1 |  |  |  |  |
|  | 1332 | 85.1 | 25.9 | 178 | 265.1 |  |  |  |  |
|  | 1337 | 86.2 | 25.7 | 181 | 265.9 |  |  |  |  |
|  | 1343 | 86.6 | 26.3 | 181 | 265.9 |  |  |  |  |
|  | 1347 | 88.2 | 26.8 | 184 | 265.5 |  |  |  |  |
|  | 1351 | 90.6 | 27.7 | 188 | 265.7 |  |  |  |  |
|  | 1355 | 93.0 | 28.3 | 193 | 265.9 |  |  |  |  |
|  | 1356 | 93.8 | 28.4 | 193 | 266.2 |  |  |  |  |
|  | 1360 | 93.6 | 28.4 | 193 | 266.5 |  |  |  |  |
|  | 1366 | 93.6 | 28.4 | 191 | 266.6 |  |  |  |  |
|  | 1369 | 94.4 | 28.7 | 195 | 266.2 |  |  |  |  |
|  | 1373 | 97.5 | 29.5 | 199 | 266.6 |  |  |  |  |
|  | 1376 | 99.2 | 30.0 | 204 | 266.7 |  |  |  |  |
|  | Stabilization |  |  |  |  |  |  |  |  |
|  | 1384 | 99.7 | 30.1 | 203 | 267.3 |  |  |  |  |
|  | 1394 | 99.6 | 30.1 | 202 | 267.3 |  |  |  |  |
|  | 1400 | 99.2 | 30.0 | 200 | 267.3 |  |  |  |  |
|  | 1406 | 99.3 | 30.0 | 199 | 267.3 |  |  |  |  |
|  | 1409 | 99.2 | 30.0 | 198 | 267.3 |  |  |  |  |
|  | 1415 | 99.1 | 30.0 | 196 | 267.2 |  |  |  |  |
|  | 1421 | 98.9 | 29.9 | 195 | 267.2 |  |  |  |  |
|  | 1425 | 98.8 | 29.9 | 194 | 267.2 |  |  |  |  |
|  | 1433 | 98.9 | 29.9 | 193 | 267.2 |  |  |  |  |
|  | 1437 | 98.8 | 29.9 | 192 | 267.2 |  |  |  |  |
|  | 1442 | 98.9 | 29.9 | 191 | 267.2 |  |  |  |  |
|  | 1453 | 99.2 | 30.0 | 190 | 267.2 |  |  |  |  |
|  | 1459 | 98.9 | 29.9 | 189 | 267.2 |  |  |  |  |
|  | 1467 | 99.3 | 30.0 | 188 | 267.2 |  |  |  |  |
|  | 1475 | 99.1 | 30.0 | 187 | 267.2 |  |  |  |  |
|  | 1487 | 99.2 | 30.0 | 186 | 267.2 |  |  |  |  |
|  | 1502 | 99.6 | 30.1 | 186 | 267.2 |  |  |  |  |
|  | 1522 | 99.6 | 30.1 | 185 | 267.3 |  |  |  |  |
|  | 1540 | 99.6 | 30.1 | 184 | 267.3 |  |  |  |  |
|  | 1565 | 99.3 | 30.0 | 183 | 267.3 |  |  |  |  |
|  | 1596 | 99.3 | 30.0 | 182 | 267.3 |  |  |  |  |
|  | 1660 | 99.7 | 30.1 | 182 | 267.3 |  |  |  |  |
|  | 1720 | 99.4 | 30.1 | 182 | 267.3 |  |  |  |  |
|  | 1765 | 99.3 | 30.0 | 183 | 267.2 |  |  |  |  |
|  | 1780 | 99.2 | 30.0 | 184 | 267.2 |  |  |  |  |
|  | 1795 | 99.3 | 30.0 | 185 | 267.2 | 3.15 | BAC - actual (measured value) |
|  | 1810 | 99.3 | 30.0 | 185 | 267.2 |  |  |  |  |
|  | 1825 | 99.5 | 30.1 | 186 | 267.3 |  |  |  |  |
|  | 1840 | 99.4 | 30.1 | 186 | 267.3 |  |  |  |  |
|  | 1855 | 99.5 | 30.1 | 187 | 267.3 |  |  |  |  |
|  | 1870 | 99.7 | 30.2 | 187 | 267.3 |  |  |  |  |
|  | 1885 | 99.5 | 30.1 | 187 | 267.3 |  |  |  |  |
|  | 1900 | 99.8 | 30.2 | 189 | 267.3 |  |  |  |  |
|  | 1915 | 99.7 | 30.2 | 189 | 267.3 |  |  |  |  |
|  | 1930 | 99.7 | 30.2 | 190 | 267.3 |  |  |  |  |
|  | 1945 | 99.7 | 30.2 | 190 | 267.3 |  |  |  |  |
|  | 1960 | 99.6 | 30.1 | 191 | 267.3 |  |  |  |  |
|  | 1975 | 99.6 | 30.1 | 192 | 267.3 |  |  |  |  |
|  | 1990 | 99.7 | 30.1 | 192 | 267.3 |  |  |  |  |
|  | 2005 | 99.8 | 30.2 | 193 | 267.4 |  |  |  |  |
|  | 2020 | 99.6 | 30.1 | 193 | 267.4 |  |  |  |  |
|  | 2035 | 99.8 | 30.2 | 194 | 267.4 |  |  |  |  |
|  | 2050 | 99.7 | 30.2 | 195 | 267.3 |  |  |  |  |
|  | 2065 | 100.0 | 30.2 | 196 | 267.4 |  |  |  |  |
|  | 2080 | 100.0 | 30.2 | 196 | 267.3 |  |  |  |  |
|  | 2095 | 99.5 | 30.1 | 195 | 267.3 |  |  |  |  |
|  | 2110 | 99.5 | 30.1 | 195 | 267.2 |  |  |  |  |
|  | 2125 | 99.5 | 30.1 | 195 | 267.2 |  |  |  |  |
|  | 2140 | 99.6 | 30.1 | 196 | 267.3 |  |  |  |  |
|  | 2200 | 99.7 | 30.1 | 198 | 267.2 |  |  |  |  |
|  | 2260 | 99.7 | 30.1 | 200 | 267.1 |  |  |  |  |
|  | 2320 | 100.0 | 30.2 | 203 | 267.2 |  |  |  |  |
|  | 2380 | 99.7 | 30.1 | 204 | 267.2 |  |  |  |  |
|  | 2440 | 99.7 | 30.1 | 207 | 267.2 |  |  |  |  |
|  | 2500 | 100.0 | 30.2 | 207 | 267.2 |  |  |  |  |
|  | 2560 | 100.0 | 30.2 | 208 | 267.2 |  |  |  |  |
|  | 2620 | 100.0 | 30.2 | 210 | 267.2 |  |  |  |  |
|  | 2680 | 100.0 | 30.2 | 213 | 267.2 |  |  |  |  |

How to model the changes of boron acid concentration

during the tests

There were two changes of boron acid concentration (BAC). One of them was during the test number 4 and second one during the test number 5. We calculated the critical position of bank 6 and critical BAC was calculated only for state before start of the tests (Tef = 125.00 days, position of bank 6 191 cm, inlet temperature 267.2 deg., power level 100 %). The BAC was not changed during the modelling of the 1st, 2nd, 3rd, 6th test and during the stabilization after the tests in the MOBY-DICK input data files. The continual measurement of the BAC was not on during the tests. We know only total change of the BAC but not trend of the change. Therefore we have to find optimal modelling of the BAC change. It is following:

|  | Test No. 4 |  | Test No. 5 |
| --- | --- | --- | --- |
|  | time [min] | (cB [g/kg] |  | time [min] | (cB [g/kg] |
|  | 551 552 553 554 555 556 557 558 559 | +0.01 +0.01 +0.01 +0.01 +0.01 +0.01 +0.01 +0.01 +0.01 |  | 900 904 907 910 912 949 961 969 979 989 | +0.01 +0.01 +0.01 +0.01 +0.01 +0.01 +0.01 +0.01 +0.01 +0.01 |

References

[1]	Krysl V., Mikolas P., Lehman M., Pecka M., Bajgl J.: Short Description of the Program MOBY-DICK and First Experience of its Application to 3D Pin-to-Pin Calculations. The International Conference on Reactor Physics and Reactor Computations, January 1994, Tel Aviv, Israel.

[2]	Krysl V., Lehman M.: MOBY-DICK User`s Manual. 1991, Plzeň ZJS-2/91.

[3]	Mikolas, P: Proposal on Benchmark for VVER-440 FA Burn-up Comparison. Proccedings of the sixth Symposium of AER, Kirkkonummi, Finland, 1996.